## Slide 1: Some important Guidelines(Which need to be considered for our project)
Routine data for the following is to be collected in separate forms as per frequency prescribed:-
 Reservoir water surface elevation.
 Reservoir inflow.
 Spillway outflow.
 River releases.
 Irrigation, water supply and hydropower releases.
 Weather related data.
 Surveillance and monitoring
 Water quality Further records of the following operations
(Source) https://damsafety.in

## Slide 2: Some important Guidelines(Which need to be considered for our project)
These records would be helpful in identifying development of any unusual conditions in the
Dam.
Operations of the spillway gates and outlet works.  Operating hours of mechanical equipment‘s.
 Testing/Operation of spillway gates, stop-logs and associated controls.
 Testing/operation of Outlet gates, valves and associated controls,
 Maintenance activities carried out.
 Reservoir and dam inspections.
 Unusual conditions or occurrences, including acts of vandalism.
 Attendance statement at the dam during emergency operations.
 Changes to normal operating procedures.
 Communication network checks.
 Safety and special instructions.
 Names and addresses of official visitors (e.g. staff carrying out inspection)
 Any other item pertaining to the operation and maintenance of the dam

## Slide 3: Some important Guidelines(Which need to be considered for our project)
Instructions for Operating Control Mechanisms
The correct method and sequence of opening and closing guard gates, gate usage during low and high flow, and openings at which excessive vibration are experienced, and operating problems peculiar to a specific gate should also be listed

## Slide 4: Some important Guidelines(Which need to be considered for our project)
Release of Surplus Water
If reservoir levels increase beyond the levels indicated above on or before the prescribed dates, the radial gate shall be cautiously opened by issuing warning by sirens and wireless messages to all concerned authorities as prescribed. By 15th September the reservoir should be near about FRL as after 15th September, the river discharge reduces considerably and there are little chances of filling the reservoir after this date. During very high flood when reservoir water is at FRL, the incoming flood will have to be passed over spillway taking care that rate of out flow does not exceed the rate of inflow in the reservoir. The absorption between FRL 348.55 m and MWL 351.45 m is 289 M. cu.m. and the moderated discharge of the spillway is 6825.00 cumec. The rate of rise of reservoir water level may be restricted to 10 cm / hour after FRL so that the flood can be safely moderated and regulated for the prolonged period of about 30 hours, without crossing MWL, thereby reducing spillway discharge and minimizing downstream damages

## Slide 5: Inflow forecasting
Inflow forecasting should include instructions and procedure for preparing, periodic estimates of inflow volumes especially for the monsoon season. These estimates provide a basis to plan reservoir and project operations before and during the flood season and to permit optimization and coordination of water supply and other reservoir functions. Also, these estimates will help in planning operating procedures consistent with operating criteria to protect the dam and its appurtenances against failure caused by high reservoir water levels and excessive discharge rates. The instructions and